Product Descriptions

Metraline Pro-Typ EM II Test Adapter for Electric Charging Points

Single and 3-phase test adapter with type 2 plug for testing the effectiveness of protective measures at electric charging points with the Profitest Master, simulation of fictitiously connected electric vehicles and current-carrying capacity per IEC 61851-1. Extended CP test pin for testing charging points with permanently attached charging cable.

Vehicle simulation (CP)

- Vehicle states A through E are selected with a rotary switch.

Cable simulation (PP)

- The various codings for charging cables with 13, 20, 32 and 63 A, as well as "no cable connected", can be simulated with the help of a rotary switch.

Fault simulation

- Simulation of a short-circuit between CP and PE by means of a rotary switch

Indication of phase voltages via LEDs

- Depending on the charging station, either one or three phases can be active.

- Testing of electric charging stations with permanently attached charging cable by means of an extended CP test pin

Regarding vehicle simulation (CP)

States A, B, C and E can be simulated in accordance with IEC 61851. The various vehicle states are selected by means of a rotary switch.

- State A - no vehicle connected

- State B - vehicle connected but not ready for charging

- State C - vehicle connected and ready for charging, venting of the charging area not required

- State E - error: Short circuit between CP and PE via internal diode

Regarding cable simulation (PP)

The various codings for charging cables with 13, 20, 32 and 63 A can be simulated. It's also possible to simulate the "no cable" state.

The various charging cables are simulated by connecting different resistances between PP and PE with the help of a rotary switch. The following values are possible in accordance with IEC 61851:

- No cable - 0 Ω

- 13 A cable - 1.5 kΩ

- 20 A cable - 680 Ω

- 32 A cable - 220 Ω

- 63 A cable - 100 Ω

Delivery

1x METRALINE PRO-TYP EM I test adapter

1x set of operating instructions

Product Code: Z525F